## ASHRAE Standard 901G_2010
// This table saved as App3-4A_SpaceBySpace-S901G_2010.csv | [17 empty] | IllumSetptMin
TABLE SpaceFunctionData
| FuncType | OccDens | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHrlyUsePerPers | IntLPDReg | RCRThresh | S6212010_CodeVentPerArea | S6212010_CodeVentPerPerson | S6212010_CodeExhPerArea | IMC2012_CodeVentPerArea | IMC2012_CodeVentPerPerson | IMC2012_CodeExhPerArea | T24N2013_CodeVentPerArea | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef | ;
| //SpaceBySpace | # per 1000 ft² | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² |  | CFM/ft² | CFM/person | CFM/ft² | CFM/ft² | CFM/person | CFM/ft² | CFM/ft² | Btu/h-ft2 | W/ft2 | lux | lux |  |  |  | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule | ;
| Unoccupied-Exclude from Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Unoccupied-Include in Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Atrium - First 40 ft in height | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.03 | NotApplicable | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Atrium - Height above 40 ft | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.02 | NotApplicable | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Attic or Crawlspace (Naturally or Mechanically Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Attic or Crawlspace (Not Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For auditorium | 142.8571 | 245 | 105 | 1 | 0.09 | 0.79 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For Performing Arts Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 2.43 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For Motion Picture Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.14 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Classroom/Lecture/Training | 50 | 245 | 155 | 1 | 0.18 | 1.24 | 4 | 0.12 | 10 | 0 | 0.12 | 10 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | ;
| Conference/Meeting/Multipurpose | 66.6667 | 245 | 155 | 1 | 0.09 | 1.23 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Copy Room | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.5 | 0 | 0 | 0.06 | 5 | 0.5 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.66 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Dining Area | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.65 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dining Area - For Bar Lounge/Leisure Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.31 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dining Area - For Family Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.89 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dressing/Fitting Room for Performing Arts Theater | 20 | 255 | 475 | 0.5 | 0.578 | 0.4 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Electrical/Mechanical | 3 | 250 | 250 | 3 | 0 | 0.95 | 6 | 0 | 0 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Employee Breakroom | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Food Preparation | 5 | 275 | 475 | 1.5 | 0.578 | 0.99 | 6 | 0.12 | 7.5 | 0 | 0 | 0 | 0.7 | 0.15 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Laboratory - For Classrooms | 10 | 250 | 200 | 2 | 0.18 | 1.28 | 6 | 0.18 | 10 | 0 | 0.18 | 10 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt | ;
| Laboratory - For Medical/Industrial/Research | 10 | 250 | 200 | 2 | 0.18 | 1.81 | 6 | 0.18 | 10 | 0 | 0.18 | 10 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt | ;
| Lobby | 10 | 250 | 250 | 0.5 | 0.09 | 0.9 | 4 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Elevator | 10 | 250 | 250 | 0.5 | 0.09 | 0.64 | 6 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Performing Arts Theater | 10 | 250 | 250 | 0.5 | 0.09 | 2 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Motion Picture Theater | 10 | 250 | 250 | 0.5 | 0.09 | 0.52 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Locker Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.75 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Office - Enclosed | 10 | 250 | 200 | 1.5 | 0.18 | 1.11 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Office - Open Plan | 10 | 250 | 200 | 1.5 | 0.18 | 0.98 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Restrooms | 10 | 250 | 250 | 0.2 | 0 | 0.98 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Sales Area (for accent lighting, see Section 9.6.2 (b)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 0.12 | 7.5 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Stairway | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.63 | 6 | 0.06 | 5 | 0 | 0.12 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Workshop | 10 | 275 | 475 | 1 | 0.18 | 1.59 | 6 | 0.12 | 7.5 | 0 | 0.18 | 10 | 0.5 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Automotive - Service/Repair | 10 | 275 | 475 | 1 | 0.18 | 0.67 | 4 | 0.12 | 7.5 | 1.5 | 0 | 0 | 0.75 | 1.5 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Bank/Office - Banking Activity Area | 10 | 250 | 250 | 1.5 | 0.18 | 1.38 | 6 | 0.06 | 7.5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Convention Center - Audience Seating | 66.6667 | 245 | 155 | 1 | 0.09 | 0.82 | 4 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Convention Center - Exhibit Space | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.45 | 4 | 0.06 | 7.5 | 0 | 0.06 | 10 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Courtroom | 10 | 250 | 200 | 1.5 | 0.18 | 1.72 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Confinement Cells | 10 | 250 | 250 | 0.5 | 0.192 | 1.1 | 6 | 0.12 | 5 | 0 | 0.12 | 5 | 1 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Judges’ Chambers | 10 | 250 | 200 | 1.5 | 0.18 | 1.17 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Classroom | 50 | 245 | 155 | 1 | 0.18 | 1.34 | 4 | 0.12 | 10 | 0 | 0.12 | 10 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.07 | 6 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dormitory - Living Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.38 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Fire Stations - Engine Room | 3 | 250 | 250 | 3 | 0 | 0.56 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Fire Stations - Sleeping Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.25 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Fitness Area 0.72 4 | 66.6667 | 255 | 875 | 0.5 | 0.18 | 0.72 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Gymnasium Audience Seating 0.43 6 | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Playing Area 1.20 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hospital - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.89 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Hospital - Emergency | 10 | 250 | 200 | 1.5 | 0.24 | 2.26 | 6 | 0 | 15 | 0 | 0 | 30 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Exam/Treatment | 10 | 250 | 200 | 1.5 | 0.24 | 1.66 | 8 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Laundry/Washing | 10 | 250 | 250 | 3 | 0.18 | 0.6 | 4 | 0.12 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.3 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Hospital - Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 1.07 | 6 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hospital - Medical Supply | 10 | 250 | 200 | 1.5 | 0.24 | 1.27 | 6 | 0.18 | 5 | 0 | 0.18 | 5 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Nursery | 10 | 250 | 200 | 1.5 | 0.24 | 0.88 | 6 | 0 | 0 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Nurses’ Station | 10 | 250 | 200 | 1.5 | 0.18 | 0.87 | 6 | 0.06 | 5 | 0 | 0 | 15 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Hospital - Operating Room | 10 | 250 | 200 | 1.5 | 0.24 | 1.89 | 6 | 0 | 30 | 0 | 0 | 30 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Patient Room | 10 | 250 | 200 | 1.5 | 0.24 | 0.62 | 6 | 0 | 25 | 0 | 0 | 25 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Pharmacy | 10 | 250 | 200 | 1.5 | 0.24 | 1.14 | 6 | 0.18 | 5 | 0 | 0.18 | 5 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Physical Therapy | 10 | 250 | 200 | 1.5 | 0.24 | 0.91 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Radiology/Imaging | 10 | 250 | 200 | 1.5 | 0.24 | 1.32 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Recovery | 10 | 250 | 200 | 1.5 | 0.24 | 1.15 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.82 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 1.11 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Lobby | 10 | 250 | 250 | 0.5 | 0.18 | 1.06 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hotel/Highway Lodging - Highway Lodging Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.88 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Hotel/Highway Lodging - Highway Lodging Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 0.75 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Library - Card File and Cataloging | 10 | 250 | 200 | 1.5 | 0.18 | 0.72 | 4 | 0.12 | 5 | 0 | 0.12 | 5 | 0 | 0.15 | 0 | 0 | 200 | 300 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Library - Reading Area | 20 | 250 | 200 | 1.5 | 0.18 | 0.93 | 4 | 0.12 | 5 | 0 | 0.12 | 5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Manufacturing - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.41 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Manufacturing - Detailed Manufacturing 1.29 4 | 10 | 250 | 200 | 1 | 0.18 | 1.29 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - Equipment Room 0.95 6 | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.05 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - High Bay (25–50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.23 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - Low Bay (<25 ft Floor to Ceiling Ht) | 10 | 275 | 475 | 1 | 0.18 | 1.19 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Multifamily - Dwelling/Sleeping Units | 5 | 245 | 155 | 0.5 | 0 | As Designed | NotApplicable | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Museum - General Exhibition | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.05 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Museum - Restoration | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.02 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Parking Garage - Garage Area | 10 | 250 | 200 | 0 | 0 | 0.19 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | ;
| Post Office - Sorting Area | 10 | 250 | 200 | 1 | 0.18 | 0.94 | 4 | 0.12 | 7.5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Religious Buildings - Audience Seating | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Religious Buildings - Fellowship Hall | 142.8571 | 245 | 105 | 0.5 | 0.09 | 0.64 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Religious Buildings - Worship Pulpit, Choir | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Retail - Dressing/Fitting Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.87 | 8 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Retail - Mall Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.1 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Retail - Sales Area (for accent lighting, see Section 9.6.3(c)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 0.12 | 7.5 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Sports Arena - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 0.72 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 3 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 2 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.92 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 1 | 142.8571 | 245 | 105 | 1 | 0.09 | 3.01 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Ring Sports Arena | 142.8571 | 245 | 105 | 1 | 0.09 | 2.68 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Transportation - Air/Train/Bus—Baggage Area | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.76 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Transportation - Airport—Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.36 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Transportation - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.54 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Transportation - Terminal—Ticket Counter | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.08 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Warehouse - Fine Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.06 | 10 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Warehouse - Medium/Bulky Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.58 | 4 | 0.06 | 10 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;